In addition to being a warning flag for amateur workmanship, improper double taps are bad because of the uncertainty of their connections. If the connection isn’t designed for two wires, it can overheat. Even if the connection is secure, there’s a chance that the second circuit might overload the breaker. They also make it impossible to isolate individual circuits. Remedies for double taps can range from very simple (adding a pigtail) to moderately simple (adding a breaker) to complex (replacing the panel). An electrician should make the decision about how to fix an improper double tap.

Question: Which panels are designed to accept two wires to a circuit? Is there a limit to how many neutral wires you can cram into one hole of the bus bar? Is this the same as double tapping the hot wires?

Answer: There aren’t any panels that are designed to accept two wires to a circuit but there are some Square D and some Cutler Hammer breakers that are. Both only allow double tapping with copper wire, not aluminum. There are restrictions having to do with wire size and torque. Also, neutral terminal bars can have two or three grounding wires connected to an individual lug – depending on size – but only one neutral wire per lug.

# Square D

Some (not all) Square D breakers are designed to accept two wires. They’re easy to spot; the terminal has a saddle with two channels that are obviously intended to hold two wires. Remember that, while the saddle-type of breaker is designed to hold two wires, the wires must be between #10 and #14 AWG. Also remember that all breaker lugs are supposed to be tightened to a specified torque. Most breakers require about 25 in-lbs (more or less depending on wire size). But the two-wire Square D breakers require 36 in-lbs. This is quite tight.

## Cutler Hammer

Some Cutler Hammer breakers (not all) allow two wires to be attached to their terminals. The wires must be between #10 and #14 AWG, and the screws must be tightened to 30 in-lbs. These are much harder to identify than the Square D breakers are. They’re the type CH breakers and they’ll say so on the small paper label just above the lug screw, but it’s very tiny and hard to read. Another way to tell is to look for a chart, cast into the breaker’s plastic body, that lists how many wires of what size can be connected to it. If the breaker’s installed in a panel, you can look underneath the lowest breaker on the right side to try to see this chart.

# Neutral Terminal Bars

Neutral terminal bars are easier. They can have only one neutral wire (proper term “grounded conductor”) per terminal. However, they can have one, two or three grounding conductors (proper term “grounding conductors”) per terminal, depending on the size of the conductors.

There are two reasons for this. First, having more than one neutral wire on a lug makes it impossible to isolate the two circuits when working on them. It’ll be necessary to de-energize both circuits instead of one. Worse yet, if one serves a multi-wire circuit, then inadvertently disconnecting it will have the effect of putting 240 volts on each of the 120-volt halves of the circuit. The second reason has to do with the physical integrity of the connection and the build-up of heat if this connection isn’t secure. These terminals are only listed and labeled to secure a single current carrying conductor. Neutral wires are intended to carry current during normal use. The grounding conductors only carry current when there’s a problem and only for a short time so heat build-up at the terminal shouldn’t be an issue. Double tapped grounded wires (neutrals) are incorrect for exactly the same reason as double tapped ungrounded wires (hot wires) are.

In case you’re interested, UL 67 has always required the one-neutral-per-terminal rule but the NEC has only specifically articulated that requirement since 2002. (See the attached code panel log.)

Log from the NEC Code Panel, regarding the new clarifying language in the Code.

(Log #3287) 9- 113 - (384-21 (New) ): Accept

SUBMITTER: James T. Pauley, Square D Co.

RECOMMENDATION: Add a new 384-21 to read as follows:

384-21. Grounded Conductor Terminations. Each grounded conductor shall terminate within the

panelboard in an individual terminal that is not also used for another conductor. Exception: Grounded conductors of circuits with parallel conductors shall be permitted to terminate in a single terminal if the terminal is identified for connection of more than one conductor.

SUBSTANTIATION: This revision is needed to coordinate the installation requirements with a long standing product standard requirement. Clause 12.3.10 of UL 67 (Panelboards) states “An individual terminal shall be provided for the connection of each branch-circuit neutral conductor.” The requirement has been enforced in the past by a close review of the manufacturers markings and by NEC 110-3(b). However, since it is a rule that specifically effects how the installer can make connections, it is important that it be in the NEC. Even with the manufacturers markings, inspectors still indicate that they see a number of panelboards installed with two (or more) branch circuit neutrals under one terminal or they see an equipment grounding conductor and neutral under the same terminal.

There is very good rationale for the requirement in the product standards. Doubling up on the neutrals creates a significant problem when the circuit needs to be isolated. In order to isolate the circuit, the branch breaker is turned off and the neutral is disconnected by removing it from the terminal. If the terminal is shared with another circuit, the connection on the other (still energized) circuit will be loosened as well. This can wreak havoc, particularly if the neutral is part of a 120/240V multi-wire branch circuit. Also, the neutral assemblies are not evaluated with doubled-up neutrals in the terminals. The connection of a neutral and equipment grounding conductor creates a similar issue. One of the objectives of the particular arrangement of bonding jumpers, neutrals and equipment grounds is to allow circuit isolation while keeping the equipment grounding conductor still connected to the grounding electrode (see UL 896A - Reference standard for Service Equipment). When the neutral is disconnected, the objective is to still have the equipment ground solidly connected to the grounding electrode. If both the neutral and grounding conductor are under the same terminal, this cannot be accomplished. This addition to the NEC does not change any product or permitted wiring arrangement from what it is today. It will however, it will help installers to avoid wiring the panel in violation of 110- 3(b) and then have to contend with a red-tag from the inspector. The code language is proposed in a fashion to allow consistent enforcement of the provision by the AHJ. Although the UL wording is adequate for the product standard, it is important that the NEC language is as clear an unambiguous as possible. This is the reason for specifically noting that the terminal cannot be used for another conductor. Furthermore, the code requirement has been worded to make sure that both branch circuit and feeder neutrals are covered since it is not uncommon to have feeder breakers as well as branch breakers in the panelboard (the issue for the neutral is the same regardless of branch or feeder). Also, the term “grounded conductor” is used to be consistent with the code terminology and to recognize that not all grounded conductors are neutrals. An exception has been proposed to avoid any confusion relative to parallel circuit arrangements. In these instances, multiple neutrals could be in a single terminal if the terminal has been identified as acceptable for multiple conductors.

PANEL ACTION: Accept.

NUMBER OF PANEL MEMBERS ELIGIBLE TO VOTE: 11

VOTE ON PANEL ACTION:

AFFIRMATIVE: 11