| Inspecting Air-Conditioning Systems |  |
| --- | --- |

Looking down into an outdoor compressor unit with the top cover removed. The compressor is on the upper right, controls are on the lower right, and the fan and condenser coils are to the left.

The capacity of an existing heating or cooling system, as measured by its ability to heat or cool a specific building or space, can be determined in either of two ways:

- Field Test.  Properly sized heating and cooling systems should operate at full capacity at normal yearly outside temperature extremes and should be slightly undersized for unusual outside temperature extremes. It is rare, however, that they can be checked under such conditions.

Test: Operate the heating system on the coolest possible day and the cooling system on the warmest possible day (within the limitations of the inspection period). Note how "hard" the system is working to maintain the preset indoor temperature, as indicated by how often the system cycles on and off, and compare this to outside temperatures.

This procedure, while inexact, may provide some idea of the system's potential capacity. When the system has a history of continuous use, maintenance, and repair, it can be assumed to have sufficient capacity. However, check with present or former building tenants on this matter. Of more concern is the fuel efficiency of the system. Ask the local utility company or fuel distributor for records of past fuel consumption and consider this in the overall assessment of the HVAC system.

2) Design calculation. An HVAC system's capacity can be more accurately determined by noting its heating or cooling output (in tons or BTUs) from information on the manufacturer's data plate and comparing it to the building's heating and cooling loads. These loads can be calculated using the Air Conditioning Contractors of America's Manual or similar load calculation guide.

A rough estimate of a building's required heating equipment size in BTUs per hour (BTUH) can be obtained by using the following formula:

BTUH = .33 x [square footage of building to be heated] x [difference between outside and inside design temperatures]

The factor of .33 in this formula is based on R11 exterior walls, an R19 ceiling at the top floor or roof, and double-glazed windows. A rough estimate of a building's required cooling equipment size, in tons, can be made by dividing the floor area by 550 (each ton equals 12,000 BTUH). Tonnage is not an adequate measure of cooling capacity in a dwelling of three or more floors with the air handling unit located on the lowest floor, with such a layout, the top floor can never be properly cooled. These estimates should be followed by a complete load calculation after rehabilitation needs are firmly established.

# Central Air Conditioning Systems

Central air conditioning systems are defined here as electrically operated refrigerant-type systems used for cooling and dehumidification. Heat pumps are similar to central air conditioners, but are reversible and can also be used as heating devices. Air conditioning systems should be tested only when the outside air temperature is above 65 F (18 C); below that temperature, the systems will not operate properly and may shut down due to safety controls.

There are two types of central air conditioning systems: integral and split.

In the integral system, all mechanized components -- compressor, condenser, evaporator, and fans -- are contained in a single unit. The unit may be located outside the building with its cold air ductwork extending into the interior, or it may be located somewhere inside the building with its exhaust air ducted to the outside.

In the split system, the compressor and condenser are located outside the building and are the evaporator is placed either directly above or below the furnace, depending on the furnace design. Assess the condition of central air conditioning systems as follows:

Compressor and condenser. The compressor pumps refrigerant gas under high pressure through a condenser coil, where it gives up heat and becomes a liquid. The heat is exhausted to the outside air by the condenser fan. Compressors have a service life of 5 to 15 years, depending on the maintenance they receive, and are the most critical component in the air conditioning system.

Test: Activate the system and observe the operation of the compressor. It should start smoothly and run continuously; noisy start up and operation indicates a worn compressor. The condenser fan should start simultaneously with the compressor. After several minutes of operation, the air flowing over the condenser should be warm. If it isn't, either the compressor is faulty or there is not enough refrigerant in the system.

If the compressor, condenser, and condenser fan are part of a split system and are located in a separate unit outside, check the air flow around the outside unit to make sure it is unobstructed. Look for dirt and debris inside the unit, particularly on the condenser coils and fins, and inspect all electrical wiring and connections. The unit should be level and well-supported, and its housing intact and childproof. An electrical disconnect switch for use during maintenance and repairs should be located within sight of the unit. Integral systems located somewhere on or in the buildng should have their compressors placed on vibration mountings to minimize sound transmission to inhabited building spaces.

Refrigerant lines. Refrigerant lines form the link between the interior and exterior components of a split system. The larger of the two lines carries low pressure (cold) refrigerant gas from the evaporator to the compressor. It is about the diameter of a broom handle and should be insulated along its entire length. The smaller line is uninsulated and carries high pressure (warm) liquid refrigerant to the evaporator.

Check both lines for signs of damage and make sure the insulation is intact on the larger line. On its exterior, the insulation should be protected from ultraviolet damage by a covering or by white paint. Sometimes a sight glass is provided on the smaller line; if so, the flow of refrigerant should look smooth through the glass. Bubbles in the flow indicate a deficiency of refrigerant in the system. Frost on any exposed parts of the larger line also indicates a refrigerant deficiency.

Seismic vulnerability. If the building is in seismic zones 3 or 4 (California and portions of Alaska, Arkansas, Hawaii, Idaho, Missouri, Montana, Nevada, Oregon, Utah, Wyoming, and Washington), check roof-mounted compressor and condenser units for the presence of seismic bracing to the structure.

Evaporator. The evaporator is enclosed in the air distribution ductwork and can only be observed by removing a panel or part of the furnace plenum. High pressure liquid refrigerant enters the evaporator and expands into a gas, absorbing heat from the surrounding air. Air is pushed past the evaporator coil by the system's circulation blower; in the process, water vapor from the air condenses on the evaporator coil and drips into a drain pan. From there, it is directed to a condensate drain line that may sometimes include a condensate pump. The drain line empties into a house drain or directly to the building's exterior.

Examine the ductwork around the evaporator for signs of air leakage and check below the evaporator for signs of water leakage due to a blocked condensate drain line. Such leakage can present a serious problem if the evaporator is located above a warm air furnace, where dripping condensate water can rust the heat exchanger, or above a ceiling, where it can damage the building components below.

Follow the condensate line and make sure that it terminates in a proper location. If there is a pump on the line, check its operation. In split systems where the evaporator is located in an attic or closet, the condensate drain pan should have an auxiliary condensate drain line located above the regular drain line or an auxiliary drain pan that is separately drained. The connection of a condensate drain line to a plumbing vent in the attic may violate local codes. Check for such violations.

A leaking condensate tray

Test: If the evaporator coil can be exposed, inspect it for frost build up after about 30 minutes of operation. Frost is an indication of inadequate airflow due to dirt on the coil or a deficiency of refrigerant in the system. Check to see if water is discharging from the condensate drain line. If it is not, either the evaporator coil is not working properly or the drain line is clogged.

Central air conditioning systems can be tested by an HVAC service technician to determine their overall condition and operational efficiency. This test requires a variety of specialized equipment and involves: 1) testing the pressure in the refrigerant lines, 2) taking amperage readings on the compressor, and 3) taking temperature readings of the air passing over the condenser and the evaporator coils, and correlating these readings with ambient outside temperature conditions.

Distribution system

Cool air distribution ductwork and controls, including zone controls, should be inspected similarly to those for forced warm air heating systems. The distribution system is made up of supply and return ducts, filters, dampers, and registers. Supply and return ducts may be made of sheet metal, glass fiber, or other materials. Glass fiber ducts are self-insulated, but sheet metal ducts are usually not insulated except where they pass through uncooled (or unheated) spaces. Sheet metal ducts are occasionally insulated on the inside; determine the presence of insulation by tapping on the duct and listening for a dull sound.

Check ducts for open joints and air leakage wherever the ducts are exposed. Examine them for dirt build up by removing several room registers and inspecting the duct. Ducts can be cleaned by a heating contractor. Supply ducts are often provided with manual dampers to balance air flow in the distribution system. Locate them by looking for small damper handles extending below the ductwork. Check their operation. In zoned systems, automatically controlled dampers may be located in the ductwork.

Test: The operation of all dampers should be checked by activating each thermostat, one at a time. If the dampers are working properly, air should begin to circulate in each zone immediately after its thermostat has been activated.

Check the location of supply and return registers in each room. Cold air registers are most effective when located high on the walls or in the ceiling (warm air registers, when positioned low on the exterior wall). Return registers should be on opposite sides of the room from supply registers. If return registers are located in a hallway or a different room, make sure intervening doors are undercut by about one inch.

Test: When the system is operating, check the air flow in all supply and return registers. Remove and inspect registers that appear blocked. Listen for sounds emanating from the duct-work and determine their source.

# Window Air Conditioners

DON'T DO THIS: Installation of this air conditioner destroyed the structural

integrity of the bearing wall between the two windows.

Window units are portable, integral air conditioning systems without ductwork. Inspect their overall condition and check the seal around each unit and its attachment to the window or wall. Ensure that it is adequately supported and look for obstructions to air flow on the exterior and for proper condensate drainage. Make sure all electrical service is properly sized and that each unit is properly grounded. Bent fins on the condenser coils may be "combed."

Test: Operate each window unit for a long enough period to determine its cooling capacity; after several minutes, the air from the unit should feel quite cool. It should start smoothly and run quietly. Check for water dripping from the condensate discharge on the exterior side of the unit. frames.

This story is adapted from the U.S. Department of Housing and Urban Development's Residential Rehabilitation Inspection Guide, 2000.